| Ref | Year | Grid | 1.Propagation 2. Distance to “responsible” asset | Geography | Tech. | Trigger | f (Hz) | Duration | Waveform | 1.Line Trip? 2. Gen Trip? | 1.Source of data 2. Processing of data 3. Analysis | 1. Causes 2.Mitigation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Gautam2024 | 2023/01 | India, Rajasthan | 1. 300 km Approx. 2. 176 km | 26°07'36.9"N 75°01'54.5"E | PV | ~ | 3.5 | Hours |  | 1.No 2.No | 1.PMU 2. Signal normalization 3.Time-response simulations with EMT models. | 1.Different PPC technologies; slow polling rates of PQ measurement; Interactions of PI controls; small dead-band of voltage ride-through. 2.Retuning |
| ESO2024 | 2021/08 | GB, Scotland | 1.Contained in Scotland 2. ~ | 57°25'30.8"N 4°15'47.8"W | WF | ~ | 8 | 25 s |  | 1.No 2.Yes | 1. PMU 2. ~ 3.Time response simulations with EMT models (TOTEM Project) | 1. A particular asset was the major contributor. 2.Mitigation measures in the asset. Retuning of voltage controllers in other assets and changes to protection settings. |
| Wang2022 | 2020/07 | Virginia, USA | 1.~ 2.~ | 37°31'32.7"N 77°26'54.1"W | PV | Daylight hours | 22 | Minutes |  | 1.No 2.No | 1.PMU; synchrophasor. 2.Spectogram; power spectral density. | 1.Active power-power factor control. 2.~ |
| Sun2025 | 2019/08 | UK | 1.Propagated across England, Wales, and some parts of Scotland. 2.120 km approx | 53°53′6″ N 1°47′27.6″ E | WF, CC | Lightning | 9 | 30 ms |  | 1.Yes 2.Yes | 1.PMU Data |  |